## Alert Criteria
ID | Alert Criteria | Report Type
1 | Physical attack that causes major interruptions or impacts to critical infrastructure facilities or to operations | Emergency Alert
2 | Cyber event that causes interruptions of electrical system operations | Emergency Alert
3 | Complete operational failure or shut-down of the transmission and/or distribution electrical system | Emergency Alert
4 | Electrical System Separation (Islanding) where part or parts of a power grid remain(s) operational in an otherwise blacked out area or within the partial failure of an integrated electrical system | Emergency Alert
5 | Uncontrolled loss of 300 Megawatts or more of firm system loads for 15 minutes or more from a single incident | Emergency Alert
6 | Firm load shedding of 100 Megawatts or more implemented under emergency operational policy | Emergency Alert
7 | System-wide voltage reductions of 3 percent or more | Emergency Alert
8 | Public appeal to reduce the use of electricity for purposes of maintaining the continuity of the Bulk Electric System | Emergency Alert
9 | Physical attack that could potentially impact electric power system adequacy or reliability; or vandalism which targets components of any security systems | Normal Report
10 | Cyber event that could potentially impact electric power system adequacy or reliability | Normal Report
11 | Loss of electric service to more than 50,000 customers for 1 hour or more | Normal Report
12 | Fuel supply emergencies that could impact electric power system adequacy or reliability | Normal Report
13 | Damage or destruction of a Facility within its Reliability Coordinator Area, Balancing Authority Area or Transmission Operator Area that results in action(s) to avoid a Bulk Electric System Emergency. | System Report
14 |  | System Report
15 | Physical threat to its Facility excluding weather or natural disaster related threats, which has the potential to degrade the normal operation of the Facility. Or suspicious device or activity at its Facility. | System Report
16 | Physical threat to its Bulk Electric System control center, excluding weather or natural disaster related threats, which has the potential to degrade the normal operation of the control center. Or suspicious device or activity at its Bulk Electric System control center. | System Report
17 | Bulk Electric System Emergency resulting in voltage deviation on a Facility; A voltage deviation equal to or greater than 10% of nominal voltage sustained for greater than or equal to 15 continuous minutes. | System Report
18 | Uncontrolled loss of 200 Megawatts or more of firm system loads for 15 minutes or more from a single incident for entities with previous year’s peak demand less than or equal to 3,000 Megawatts | System Report
19 | Total generation loss, within one minute of: greater than or equal to 2,000 Megawatts in the Eastern or Western Interconnection or greater than or equal to 1,400 Megawatts in the ERCOT Interconnection. | System Report
20 | Complete loss of off-site power (LOOP) affecting a nuclear generating station per the Nuclear Plant Interface Requirements. | System Report
21 | Unexpected Transmission loss within its area, contrary to design, of three or more Bulk Electric System Facilities caused by a common disturbance (excluding successful automatic reclosing). | System Report
22 | Unplanned evacuation from its Bulk Electric System control center facility for 30 continuous minutes or more. | System Report
23 | Complete loss of Interpersonal Communication and Alternative Interpersonal Communication capability affecting its staffed Bulk Electric System control center for 30 continuous minutes or more. | System Report
24 | Complete loss of monitoring or control capability at its staffed Bulk Electric System control center for 30 continuous minutes or more. | System Report

## J. Cause
ID | Cause
1 | Unknown
2 | Physical attack
3 | Threat of physical attack
4 | Vandalism
5 | Theft
6 | Suspicious activity
7 | Cyber event (information technology)
8 | Cyber event (operational technology)
9 | Fuel supply emergencies, interruption, or deficiency
10 | Generator loss or failure not due to fuel supply interruption or deficiency or transmission failure
11 | Transmission equipment failure (not including substation or switchyard)
12 | Failure at high voltage substation or switchyard
13 | Weather or natural disaster
14 | Operator action(s)
15 | Other

## K. Impact
ID | Impact
1 | None
2 | Control center loss, failure, or evacuation
3 | Loss or degradation of control center monitoring or communication systems
4 | Damage or destruction of a facility
5 | Electrical system separation (islanding)
6 | Complete operational failure or shutdown of the transmission and/or distribution system
7 | Major transmission system interruption (three or more BES elements)
8 | Major distribution system interruption
9 | Uncontrolled loss of 200 MW or more of firm system loads for 15 minutes or more
10 | Loss of electric service to more than 50,000 customers for 1 hour or more
11 | System-wide voltage reductions or 3 percent or more
12 | Voltage deviation on an individual facility of 10% for 15 minutes or more
13 | Inadequate electric resources to serve load
14 | Generating capacity loss of 1,400 MW or more
15 | Generating capacity loss of 2,000 MW or more
16 | Complete loss of off-site power to a nuclear generating station
17 | Other

## L. Action Taken
ID | Action Taken
1 | None
2 | Shed Firm Load: Load shedding of 100 MW or more implemented under emergency operational policy (manually or automatically via UFLS or remedial action scheme)
3 | Public appeal to reduce the use of electricity for the purpose of maintaining the continuity of the electric power system
4 | Implemented a warning, alert, or contingency plan
5 | Voltage reduction
6 | Shed Interruptible Load
7 | Repaired or restored
8 | Mitigation implemented
9 | Other